## CAL_SPECS_C
Configure This Column in CAL8816
OOC LIMIT | [14 empty] | [ DRIFT LIMIT ]
Daily Cal ü | P75/P63 | [14 empty] | P60 | [10 empty] | RATA
| 75 App_A § 5.2.1 |  |  |  | Zero level conc. - 00.0 to 20.0 % of span | [10 empty] | § 60.13.d.(1) |  | Zero level -- 00 to 20 % span | [8 empty] | Semi-annual (every 2 QA operating quarters)
| 75 App_A § 5.2.3 |  |  |  | Mid level conc. - 50.0 to 60.0 % of span | [10 empty] | § 60.13.d.(1) |  | Span level - 50 to 100 % span | [8 empty] | Parameter |  | STANDARD | [5 empty] | ATERNATE
| 75 App_A § 5.2.4 |  |  |  | High level conc. - 80.0 to 100.0 % of span | [10 empty] | § 60.13.d.(1) |  | Check the zero & span each operating day | [10 empty] | Ref |  |  |  | RA |  | CONDITION |  | mean diff
| 75 App_A § 6.3.1 |  |  |  | Perform cal error tests at both the zero and high levels | [21 empty] | SO2 |  | 75 App_A § 3.3.1 |  |  |  | 10% |  | RM avg  250 PPM |  | 15 PPM
[5 empty] | mid level in lieu of high if more rep of actual stack conc. | [10 empty] | App_F § 4.3.1 |  | OOC from the 5th 2X - PS or | [8 empty] | FLOW |  | 75 App_A § 3.3.4 |  |  |  | 10% |  | RM avg  10 fps |  | 2 fps
| 75 App_B § 2.1 |  |  |  | perform daily | [10 empty] | App_F § 4.3.1 |  | OOC back to the last good cal if 4X- PS | [8 empty] | CO2 |  | 75 App_A § 3.3.3 |  |  |  | 10% |  | none |  | 1%
| 75 App_B § 2.1.3.(a) |  |  |  | must re-cal after a failed daily cal, routine maint or cal adj | [21 empty] | O2 |  | 75 App_A § 3.3.3 |  |  |  | 10% |  | none |  | 1%
| 75 App_B § 2.1.5 |  |  |  | prospectively validated for 26 clock hours | [10 empty] | App_F Proc. 3 § 10.1.(1) |  | OPACITY - must take action at 2X PS | [8 empty] | MOISTURE |  | 75 App_A § 3.3.6 |  |  |  | 10% |  | none |  | 1.5%
| 75 App_B § 2.1.5.2 |  |  |  | Startup grace period - offline 1h & in-control before outage | [21 empty] | NOx |  | 75 App_A § 3.3.7 |  |  |  | 10% |  | RM avg  250 PPM |  | 15 PPM
Parameter | STANDARD | [5 empty] | ALTERNATE | [8 empty] | STANDARD | [6 empty] | OOC |  |  |  | NOx#/MM |  | 75 App_A § 3.3.6 |  |  |  | 10% |  | RM avg  0.2 #/MM |  | 0.02 #/MM
| Spec | [5 empty] | CONDITION |  |  |  | Spec |  |  |  |  | Performance Spec | [6 empty] | 1 day @ |  | 5 days @ |  | Annual (every 4 QA operating quarters)
NOx | 5% of span |  | 75 App_B § 2.1.4.(a) |  |  |  | span  50 PPM |  |  |  | 5.0 PPM diff |  | 75 App_B § 2.1.4.(a) |  |  | 2.5 % of span |  | 60 App_B Spec 2 § 13.1 |  |  |  |  | 10 % |  | [ 5 % ] |  | SO2 |  | 75 App_B § 2.3.1.2.(a) |  |  |  | 7.5 % |  | RM avg  250 PPM |  | 12 PPM
[7 empty] | span  200 PPM |  |  |  | 10.0 PPM diff |  | 75 App_B § 2.1.4.(a) | [13 empty] | FLOW |  | 75 App_B § 2.3.1.2.(c) |  |  |  | 7.5 % |  | RM avg  10 fps |  | 1.5 fps
SO2 | 5% of span |  | 75 App_B § 2.1.4.(a) |  |  |  | span  50 PPM |  |  |  | 5.0 PPM diff |  | 75 App_B § 2.1.4.(a) |  |  | 2.5 % of span |  | 60 App_B Spec 2 § 13.1 |  |  |  |  | 10 % |  | [ 5 % ] |  | CO |  | 60 App_B PS-4A 13.2 |  |  |  | 10% w/ RM |  | OR 5 % w/ Emis Std |  | OR 5ppm diff + 2.5 & CC
[7 empty] | span  200 PPM |  |  |  | 10.0 PPM diff |  | 75 App_B § 2.1.4.(a) | [13 empty] | CO2 |  | 75 App_B § 2.3.1.2.(a) |  |  |  | 7.5 % |  | none |  | 0.7%
O2 | 1% diff |  | 75 App_B § 2.1.4.(a) | [12 empty] | 0.5 % diff |  | 60 App_B Spec 3 § 13.1 |  |  |  |  | 2.0 % |  | [ 1 % ] |  | O2 |  | 75 App_B § 2.3.1.2.(a) |  |  |  | 7.5 % |  | none |  | 0.7%
CO2 | 1% diff |  | 75 App_B § 2.1.4.(a) | [12 empty] | 0.5 % diff |  | 60 App_B Spec 3 § 13.1 |  |  |  |  | 2.0 % |  | [ 1.0 % ] |  | MOISTURE |  | 75 App_B § 2.3.1.2.(i) |  |  |  | 7.5 % |  | none |  | 1.0%
FLOW | 6% of span |  | 75 App_B § 2.1.4.(a) |  |  |  | DP monitor |  |  |  | 0.02 "H20 diff |  | 75 App_B § 2.1.4.(a) |  |  | 3% of span |  | 60 App_B Spec 6 § 13.1 |  |  |  |  | 12.0% |  | [ 6.0 % ] |  | NOx |  | 75 App_B § 2.3.1.2.(a) |  |  |  | 7.5 % |  | RM avg  250 PPM |  | 12 PPM
INTERF. P | Pass / Fail |  | 75 App_A § 2.2.2.2 | [23 empty] | NOx#/MM |  | 75 App_B § 2.3.1.2.(a) |  |  |  | 7.5 % |  | RM avg  0.2 #/MM |  | 0.015 #/MM
MOISTURE | 1% diff |  | 75 App_B § 2.1.4.(a) | [23 empty] | HG |  | 63 App_A Table A-1 |  |  |  | 20.0 % |  | RM avg  2.5 ug/scm |  | 0.05 ug/scm
CO | [15 empty] | 5 % of span |  | 60 App_B Spec 4 § 13.1 |  |  |  |  | 20 % |  | [ 10 % ] |  | 3-LOAD RATA (atleast every 20 operating quarters)
HG | 5% of span |  | 63 App_A Table A-1 |  |  |  | (none) |  |  |  | 1.0 ug/scm diff |  | 75 App_A § 5.1.2.1 |  |  | 5 % of span |  | 60 App_B Spec 12A § 13.2 |  |  |  |  | 20 % |  | [ 10 % ] |  | FLOW |  | 3 Load Ranges seperated by at least 25% between ranges
PM | [15 empty] | 2 % of span |  | 60 App_F Proc 2 § 10.4 |  |  |  |  | 8 % |  | [ 4 % ] |  |  |  | Must do 3-load when re-linearizing monitor (i.e. When K-factor or polynomial coefficients change)
OPACITY | [15 empty] | 2 % diff |  | 60 App_B Spec 1 § 13.3.(6) |  |  |  |  | 4% |  | [ 2% ]
Weekly ü | P63 UUUUU Table A-2 On-Going QA Test Requirements | [25 empty] | RRA - Relative Response Audit
| Weekly = once every 7 operating days | [25 empty] | 63.10010(i)(2)(i) |  |  |  | Annual (every 4 calendar quarters)
| Use oxidized HG - either mid or high level | [25 empty] | P60 App_F Procedure 2 |  |  |  | 3 Runs
| If System Integrity Check (SIC) is failed, must repeat or HG OOC untill passing SIC | [29 empty] | No point is > the greatest PM CEMS Response used to develop Curve
HG | [ 10.0% of reference value ] | [5 empty] | [ 0.8 ug/scm difference ] | [23 empty] | 2 of the 3 points must fall within ±25% of regression line
If RRA cant be passed, then perform RCA
[16 empty] | Cylinder Gas Audit (CGA) | [9 empty] | ACA - Absolute Correlation Audit
Quarterly | LINEARITY | [14 empty] | Cylinder Gas Audit (CGA) | [10 empty] | ACA - Absolute Correlation Audit
| 40CFR72.2 |  |  |  | QA operating quarter = calendar quarter w/ > 168 op hrs | [10 empty] | App_F § 5.1 |  | Audit (CGA or RATA) at least once per quarter at least 2 months apart | [7 empty] | Quarterly | Quarterly | P60 App_F Procedure 2 |  |  |  | Every Calendar Quarter no closer than 2 mths
| 75 App_A § 6.2 |  |  |  | SO2 or NOX - span ≤ 30PPM - exempt from linearities | [26 empty] | Unless RRA OR RCA in same quarter
[5 empty] | Challenge each monitor @ the low, mid and high conc | [10 empty] | App_F § 5.1.2 |  | perform CGA in 3 out of the 4 quarters, | [13 empty] | 3 levels X 3 times
[5 empty] | Do not do the same level twice in succession | [12 empty] | but no more than 3 in a row | [13 empty] | Average of three responses to determine each point
[5 empty] | The duration of the linearity shall not exceed 24 op hrs | [12 empty] | audit |  | pollutant monitors |  | CO2 |  |  | O2 | [6 empty] | LOW - 0-20 Percent
| 75 App_A § 5.2.2 |  |  |  | Low level conc. - 20.0 to 30.0 % of span | [12 empty] | pt # 1 |  | 20 to 30% of span |  | 5 to 8% |  |  | 4 to 6% | [6 empty] | MID - 40-60 Percent
| 75 App_A § 5.2.3 |  |  |  | Mid level conc. - 50.0 to 60.0 % of span | [12 empty] | pt # 2 |  | 50 to 60% of span |  | 10 to 14% |  |  | 8 to 12% | [6 empty] | HIGH - 70-100 Percent
| 75 App_A § 5.2.4 |  |  |  | High level conc. - 80.0 to 100.0 % of span | [20 empty] | LEVEL | LEVEL |  |  | STANDARD |  |  |  | ALTERNATE
| 75 App_B § 2.2.1 |  |  |  | perform a linearity check at least once each QA op quarter | [20 empty] | LOW (IF Ref = Zero) | LOW (IF Ref = Zero) | [6 empty] | LE 7.5 % Applicable Std/Permit Limit
[5 empty] | conduct the linearity checks at least 30 days apart | [20 empty] | LOW (IF Ref != Zero) | LOW (IF Ref != Zero) |  |  | LE 10 % Ref Mean |  |  |  | LE 7.5 % Applicable Std/Permit Limit
| 75 App_B § 2.2.3.(e) |  |  |  | Not OOC if the linearity is aborted due to issues unrelated to the monitor's performance - forced outage | [20 empty] | MID | MID |  |  | LE 10 % Ref Mean |  |  |  | LE 7.5 % Applicable Std/Permit Limit
[26 empty] | HIGH | HIGH |  |  | LE 10 % Ref Mean |  |  |  | LE 7.5 % Applicable Std/Permit Limit
Parameter | STANDARD |  |  |  |  | ALTERNATE | [9 empty] | STANDARD |  |  | ALTERNATE
| Spec |  |  |  |  | CONDITION |  | Spec | [7 empty] | Spec |  |  | CONDITION |  |  |  |  | Spec |  |  | RCA - Relative Correlation Audit / Initial Correlation
NOx | [ LE  5 % ] | 75 App_A § 3.2 |  |  |  | none |  | [ diff  5 PPM ] |  |  |  | 75 App_A § 3.2 |  |  |  | [ > of 15% ref | 60 App_F § 5.2.3 |  | span > 50 PPM span > 20 PPM & ≤ 50 ppm span ≤ 20 PPM |  |  |  |  | [diff ≤ 5 PPM] [diff ≤ 3 PPM] [diff ≤ 2 PPM] |  |  | 63.10010(i)(2)(ii) |  |  | 3 years from completion of initial correlation
SO2 | [ LE  5 % ] | 75 App_A § 3.2 |  |  |  | none |  | [ diff  5 PPM ] |  |  |  | 75 App_A § 3.2 |  |  |  | [ > of 15% ref | 60 App_F § 5.2.3 | [9 empty] | Initial Correlation |  |  | PS-11 |  | Must be ran over 3 levels of the full operating range for unit
CO | [5 empty] | none | [9 empty] | [ > of 15% ref | 60 App_F § 5.2.3 | [14 empty] | LEVEL 1 = 0 - 50% of max concentration (Test can overlap)
O2 | [ LE  5 % ] | 75 App_A § 3.2.(1) |  |  |  | none |  | [ diff  0.5 % ] |  |  |  | 75 App_A § 3.2.(2) |  |  |  | [ > of 15% ref | 60 App_F § 5.2.3 | [14 empty] | LEVEL 2 = 25 - 75% of max concentration (Test can overlap)
CO2 | [ LE  5 % ] | 75 App_A § 3.2.(1) |  |  |  | none |  | [ diff  0.5 % ] |  |  |  | 75 App_A § 3.2.(2) |  |  |  | [ > of 15% ref | 60 App_F § 5.2.3 | [14 empty] | LEVEL 3 = 50 - 100% of max concentration (Test can overlap)
HG | [ LE  10 % ] | 75 App_A § 5.1.2.2 |  |  |  | none |  | [ diff  0.8 ug/scm ] |  |  |  | 75 App_A § 5.1.2.2 | [19 empty] | Minimum 15 valid runs may reject 5 but report ALL runs - 20 Total
Of the 15 runs, 20% need to be in the above levels
FLOW to LOAD or Gross Heat Rate | [9 empty] | Leak Check | [5 empty] | FUELFLOW to LOAD or Gross Heat Rate
75 App_B § 2.2.5.(a) |  | each QA operating quarter | [7 empty] | 75 App_B § 2.2.2 |  |  |  | DP flow monitors |  | App_D § 2.1.7 |  | optional - each fuel flow meter QA op quarter | [8 empty] | Every 3 Years |  |  | P60 Proc 2 |  | Minimum of 12 runs NOT 15
75 App_B § 2.2.5.(a).(4) |  | if 2 RATA load levels are defined as normal - use the higher | [11 empty] | Unit can be off-line |  |  |  | may be used to extend fuel flow meter cals for up to 20 calendar quarters | [13 empty] | All points can be not > the greatest CEMS value during curve
[14 empty] | 30 days apart | [17 empty] | At least 75% of 12 Points must fall within ±25% of regression line
Parameter | STANDARD | [8 empty] | Parameter |  |  |  | STANDARD |  | Parameter |  | STANDARD | [8 empty] | EPA provides a spreadsheet on selecting the best fit Correlation equation based on the data recorded. This spreadshet can be found at https://www.epa.gov/sites/production/files/2017-05/ps11qa_05042017.zip
| Avg Load |  |  | steam flow |  |  | FLOW |  | Ef | [8 empty] | Avg LOAD |  |  | eq STEAM |  | Ef
FLOW | Lavg ≥ 60 MW |  |  | 500 klb/hr |  |  | un-biased |  | 15 % | FLOW |  |  |  | Manual inspection |  | FUEL FLOW |  | Lavg > 50 MW |  |  | 500 klb/hr |  | 10%
| Lavg ≥ 60 MW |  |  | 500 klb/hr |  |  | biased |  | 10 % | [8 empty] | Lavg > 50 MW |  |  | 500 klb/hr |  | 15% |  |  |  | The 5 types of Correlation Model: | [5 empty] | 1) Linear |  |  | 2) Polynomial
| Lavg < 60 MW |  |  | 500 klb/hr |  |  | un-biased |  | 20 % | [23 empty] | 3) Logarithmic |  |  | 4) Exponential |  | 5) Power
| Lavg < 60 MW |  |  | 500 klb/hr |  |  | biased |  | 15 %
Note on BH11: For PM, data is not flagged invalid back to the previous good cal if failed. App_F Proc 2 § 10.4.1
Note on DP20: 75 App_B § 2.3.1.2.(e)
Note on DP21: 75 App_B § 2.3.1.2.(d)
Note on DP24: 75 App_B § 2.3.1.2.(h)
Note on DP26: 75 App_B § 2.3.1.2.(h)
Note on DP28: 75 App_B § 2.3.1.2.(i)
Note on AH31: Brian Perlov: For span values less than 0.3333 "wc the difference method (i.e. < 0.02 'wc ug/scm) is less restrictive.
Note on DP31: 75 App_B § 2.3.1.2.(e)
Note on DP33: 75 App_B § 2.3.1.2.(f)
Note on AH39: Brian Perlov: For span values less than 20 ug/scm the difference method (i.e. < 1.0 ug/scm) is less restrictive.
Note on X52: 10% of 8 ug/scm = 0.8 ug/scm For reference values less than 8 ug/scm the difference method (i.e. < 0.8 ug/scm) is less restrictive.
Note on BJ72: Brian Perlov: Prior to 5/30/2023 the alternative performance specification was +/- 5ppm for ALL span values.
Note on AB76: 5% of 100 ppm= 5 ppm For reference values less than 100 ppm the difference method (i.e. > 5 ppm) is less restrictive.
Note on BX76: Brian Perlov: >50 ppm (15% of reference method or +/-5ppm). For reference values of less than 33.333 ppm, the 5 ppm difference is the least restrictive. >20 ppm to <=50ppm (15% of reference method or +/-3 ppm). For reference value less than 20 ppm, the 3 ppm difference is the least restrictive. <=20ppm (15% of the reference method or +/- 2 ppm). For reference value less than 13.33 ppm, the 2 ppm difference is the least restrictive. As the highest reference gas would be 60% of 20 (i.e. 12) for all CGAs with an analyzer span of 20 or less the alternative spec would be the least restrictive. As an example: Analyzer Span of 35 ppm. Reference Gas of mid level gas could be 17.5 ppm to 21 ppm At 17.5 ppm, the 15% reference method would only allow a 2.625% error so the alternative specification of +/- 3ppm would be less restrictive. At 21 ppm, the 15% reference method would allow for 3.15% error so the reference method would be least restrictive.
Note on AB78: 5% of 100 ppm= 5 ppm For reference values less than 100 ppm the difference method (i.e. > 5 ppm) is less restrictive.
Note on AB82: 5% of 10 %= 0.5 % For reference values less than 10 % the difference method (i.e. < 0.5%) is less restrictive.
Note on AB84: 5% of 10 %= 0.5 % For reference values less than 10 % the difference method (i.e. < 0.5%) is less restrictive.
Note on B86: Brian Perlov: Part 63, Subpart UUUUU
Note on AB86: 10% of 8 ug/scm = 0.8 ug/scm For reference values less than 8 ug/scm the difference method (i.e. < 0.8 ug/scm) is less restrictive.

## CAL_SPECS_B&W
Configure This Column in CAL8816
OOC LIMIT | [14 empty] | [ DRIFT LIMIT ]
Daily Cal ü | P75/P63 | [14 empty] | P60 | [8 empty] | RATA
| 75 App_A § 5.2.1 |  |  |  | Zero level conc. - 00.0 to 20.0 % of span | [10 empty] | § 60.13.d.(1) | Zero level -- 00 to 20 % span | [7 empty] | Semi-annual (every 2 QA operating quarters)
| 75 App_A § 5.2.3 |  |  |  | Mid level conc. - 50.0 to 60.0 % of span | [10 empty] | § 60.13.d.(1) | Span level - 50 to 100 % span | [7 empty] | Parameter |  | STANDARD | [5 empty] | ATERNATE
| 75 App_A § 5.2.4 |  |  |  | High level conc. - 80.0 to 100.0 % of span | [10 empty] | § 60.13.d.(1) | Check the zero & span each operating day | [9 empty] | Ref |  |  |  | RA |  | CONDITION |  | mean diff
| 75 App_A § 6.3.1 |  |  |  | Perform cal error tests at both the zero and high levels | [19 empty] | SO2 |  | 75 App_A § 3.3.1 |  |  |  | 10% |  | RM avg  250 PPM |  | 15 PPM
[5 empty] | mid level in lieu of high if more rep of actual stack conc. | [10 empty] | App_F § 4.3.1 | OOC from the 5th 2X - PS or | [7 empty] | FLOW |  | 75 App_A § 3.3.4 |  |  |  | 10% |  | RM avg  10 fps |  | 2 fps
| 75 App_B § 2.1 |  |  |  | perform daily | [10 empty] | App_F § 4.3.1 | OOC back to the last good cal if 4X- PS | [7 empty] | CO2 |  | 75 App_A § 3.3.3 |  |  |  | 10% |  | none |  | 1%
| 75 App_B § 2.1.3.(a) |  |  |  | must re-cal after a failed daily cal, routine maint or cal adj | [19 empty] | O2 |  | 75 App_A § 3.3.3 |  |  |  | 10% |  | none |  | 1%
| 75 App_B § 2.1.5 |  |  |  | prospectively validated for 26 clock hours | [10 empty] | App_F Proc. 3 § 10.1.(1) | OPACITY - must take action at 2X PS | [7 empty] | MOISTURE |  | 75 App_A § 3.3.6 |  |  |  | 10% |  | none |  | 1.5%
| 75 App_B § 2.1.5.2 |  |  |  | Startup grace period - offline 1h & in-control before outage | [19 empty] | NOx |  | 75 App_A § 3.3.7 |  |  |  | 10% |  | RM avg  250 PPM |  | 15 PPM
Parameter | STANDARD | [5 empty] | ALTERNATE | [8 empty] | STANDARD | [5 empty] | OOC |  |  | NOx#/MM |  | 75 App_A § 3.3.6 |  |  |  | 10% |  | RM avg  0.2 #/MM |  | 0.02 #/MM
| Spec | [5 empty] | CONDITION |  |  |  | Spec |  |  |  |  | Performance Spec | [5 empty] | 1 day @ | 5 days @ |  | Annual (every 4 QA operating quarters)
NOx | 5% of span |  | 75 App_B § 2.1.4.(a) |  |  |  | span  50 PPM |  |  |  | 5.0 PPM diff |  | 75 App_B § 2.1.4.(a) |  |  | 2.5 % of span | 60 App_B Spec 2 § 13.1 |  |  |  |  | 10 % | [ 5 % ] |  | SO2 |  | 75 App_B § 2.3.1.2.(a) |  |  |  | 7.5 % |  | RM avg  250 PPM |  | 12 PPM
[7 empty] | span  200 PPM |  |  |  | 10.0 PPM diff |  | 75 App_B § 2.1.4.(a) | [11 empty] | FLOW |  | 75 App_B § 2.3.1.2.(c) |  |  |  | 7.5 % |  | RM avg  10 fps |  | 1.5 fps
SO2 | 5% of span |  | 75 App_B § 2.1.4.(a) |  |  |  | span  50 PPM |  |  |  | 5.0 PPM diff |  | 75 App_B § 2.1.4.(a) |  |  | 2.5 % of span | 60 App_B Spec 2 § 13.1 |  |  |  |  | 10 % | [ 5 % ] |  | CO |  | 60 App_B PS-4A 13.2 |  |  |  | 10% w/ RM |  | OR 5 % w/ Emis Std |  | OR 5ppm diff + 2.5 & CC
[7 empty] | span  200 PPM |  |  |  | 10.0 PPM diff |  | 75 App_B § 2.1.4.(a) | [11 empty] | CO2 |  | 75 App_B § 2.3.1.2.(a) |  |  |  | 7.5 % |  | none |  | 0.7%
O2 | 1% diff |  | 75 App_B § 2.1.4.(a) | [12 empty] | 0.5 % diff | 60 App_B Spec 3 § 13.1 |  |  |  |  | 2.0 % | [ 1.0 % ] |  | O2 |  | 75 App_B § 2.3.1.2.(a) |  |  |  | 7.5 % |  | none |  | 0.7%
CO2 | 1% diff |  | 75 App_B § 2.1.4.(a) | [12 empty] | 0.5 % diff | 60 App_B Spec 3 § 13.1 |  |  |  |  | 2.0 % | [ 1.0 % ] |  | MOISTURE |  | 75 App_B § 2.3.1.2.(i) |  |  |  | 7.5 % |  | none |  | 1.0%
FLOW | 6% of span |  | 75 App_B § 2.1.4.(a) |  |  |  | DP monitor |  |  |  | 0.02 "H20 diff |  | 75 App_B § 2.1.4.(a) | [11 empty] | NOx |  | 75 App_B § 2.3.1.2.(a) |  |  |  | 7.5 % |  | RM avg  250 PPM |  | 12 PPM
INTERF. P | Pass / Fail |  | 75 App_A § 2.2.2.2 | [21 empty] | NOx#/MM |  | 75 App_B § 2.3.1.2.(a) |  |  |  | 7.5 % |  | RM avg  0.2 #/MM |  | 0.015 #/MM
MOISTURE | 1% diff |  | 75 App_B § 2.1.4.(a) | [21 empty] | HG |  | 63 App_A Table A-1 |  |  |  | 20.0 % |  | RM avg  2.5 ug/scm |  | 0.05 ug/scm
CO | [15 empty] | 5 % of span | 60 App_B Spec 4 § 13.1 |  |  |  |  | 20 % | [ 10 % ] |  | 3-LOAD RATA (atleast every 20 operating quarters)
HG | 5% of span |  | 63 App_A Table A-1 |  |  |  | (none) |  |  |  | 1.0 ug/scm diff |  | 75 App_A § 5.1.2.1 |  |  | 5 % of span | 60 App_B Spec 12A § 13.2 |  |  |  |  | 20 % | [ 10 % ] |  | FLOW |  | 3 Load Ranges seperated by at least 25% between ranges
PM | [15 empty] | 2 % of span | 60 App_F Proc 2 § 10.4 |  |  |  |  | 8 % | [ 4 % ] |  |  |  | Must do 3-load when re-linearizing monitor (i.e. When K-factor or polynomial coefficients change)
OPACITY | [15 empty] | 2 % diff | 60 App_B Spec 1 § 13.3.(6) |  |  |  |  | 4% | [ 2% ]
Weekly ü | P63 UUUUU Table A-2 On-Going QA Test Requirements | [23 empty] | RRA - Relative Response Audit
| Weekly = once every 7 operating days | [23 empty] | 63.10010(i)(2)(i) |  |  |  | Annual (every 4 calendar quarters)
| Use oxidized HG - either mid or high level | [23 empty] | P60 App_F Procedure 2 |  |  |  | 3 Runs
| If System Integrity Check (SIC) is failed, must repeat or HG OOC untill passing SIC | [27 empty] | No point is > the greatest PM CEMS Response used to develop Curve
HG | [ 10.0% of reference value ] | [5 empty] | [ 0.8 ug/scm difference ] | [21 empty] | 2 of the 3 points must fall within ±25% of regression line
If RRA cant be passed, then perform RCA
[16 empty] | Cylinder Gas Audit (CGA) | [7 empty] | ACA - Absolute Correlation Audit | ACA - Absolute Correlation Audit
Quarterly | LINEARITY | [14 empty] | Cylinder Gas Audit (CGA)
| 40CFR72.2 |  |  |  | QA operating quarter = calendar quarter w/ > 168 op hrs | [10 empty] | App_F § 5.1 | Audit (CGA or RATA) at least once per quarter at least 2 months apart | [6 empty] | Quarterly |  | P60 App_F Proc 2 |  |  |  | Every Calendar Quarter no closer than 2 mths
| 75 App_A § 6.2 |  |  |  | SO2 or NOX - span ≤ 30PPM - exempt from linearities | [24 empty] | Unless RRA OR RCA in same quarter
[5 empty] | Challenge each monitor @ the low, mid and high conc | [10 empty] | App_F § 5.1.2 | perform CGA in 3 out of the 4 quarters, | [12 empty] | 3 levels X 3 times
[5 empty] | Do not do the same level twice in succession | [11 empty] | but no more than 3 in a row | [12 empty] | Average of three responses to determine each point
[5 empty] | The duration of the linearity shall not exceed 24 op hrs | [11 empty] | audit | pollutant monitors |  |  | CO2 |  | O2 | [6 empty] | LOW - 0-20 Percent
| 75 App_A § 5.2.2 |  |  |  | Low level conc. - 20.0 to 30.0 % of span | [11 empty] | pt # 1 | 20 to 30% of span |  |  | 5 to 8% |  | 4 to 6% | [6 empty] | MID - 40-60 Percent
| 75 App_A § 5.2.3 |  |  |  | Mid level conc. - 50.0 to 60.0 % of span | [11 empty] | pt # 2 | 50 to 60% of span |  |  | 10 to 14% |  | 8 to 12% | [6 empty] | HIGH - 70-100 Percent
| 75 App_A § 5.2.4 |  |  |  | High level conc. - 80.0 to 100.0 % of span | [18 empty] | LEVEL | LEVEL |  |  | STANDARD |  |  |  | ALTERNATE
| 75 App_B § 2.2.1 |  |  |  | perform a linearity check at least once each QA op quarter | [18 empty] | LOW (IF Ref = Zero) | LOW (IF Ref = Zero) | [6 empty] | LE 7.5 % Applicable Std/Permit Limit
[5 empty] | conduct the linearity checks at least 30 days apart | [18 empty] | LOW (IF Ref != Zero) | LOW (IF Ref != Zero) |  |  | LE 10 % Ref Mean |  |  |  | LE 7.5 % Applicable Std/Permit Limit
| 75 App_B § 2.2.3.(e) |  |  |  | Not OOC if the linearity is aborted due to issues unrelated to the monitor's performance - forced outage | [18 empty] | MID | MID |  |  | LE 10 % Ref Mean |  |  |  | LE 7.5 % Applicable Std/Permit Limit
[24 empty] | HIGH | HIGH |  |  | LE 10 % Ref Mean |  |  |  | LE 7.5 % Applicable Std/Permit Limit
Parameter | STANDARD |  |  |  |  | ALTERNATE | [9 empty] | STANDARD |  |  |  | 15% of 33.333 = 5
| Spec |  |  |  |  | CONDITION |  | Spec | [7 empty] | Spec | [7 empty] | RCA - Relative Correlation Audit / Initial Correlation
NOx | [ LE  5 % ] | 75 App_A § 3.2 |  |  |  | none |  | [ diff  5 PPM ] |  |  |  | 75 App_A § 3.2 |  |  |  | [ > of 15% ref or 5 PPM ] | 60 App_F § 5.2.3 |  |  | For O2 (4%) and CO2 (5%) equate to 40000 ppm and 50000 ppm so 15% of ref is least restrcitive. |  |  |  |  | 63.10010(i)(2)(ii) |  |  | 3 years from completion of initial correlation
SO2 | [ LE  5 % ] | 75 App_A § 3.2 |  |  |  | none |  | [ diff  5 PPM ] |  |  |  | 75 App_A § 3.2 |  |  |  | [ > of 15% ref or 5 PPM ] | 60 App_F § 5.2.3 | [7 empty] | Initial Correlation |  |  | PS-11 |  | Must be ran over 3 levels of the full operating range for unit
O2 | [ LE  5 % ] | 75 App_A § 3.2.(1) |  |  |  | none |  | [ diff  0.5 % ] |  |  |  | 75 App_A § 3.2.(2) |  |  |  | [ > of 15% ref or 5 PPM ] | 60 App_F § 5.2.3 | [12 empty] | LEVEL 1 = 0 - 50% of max concentration (Test can overlap)
CO2 | [ LE  5 % ] | 75 App_A § 3.2.(1) |  |  |  | none |  | [ diff  0.5 % ] |  |  |  | 75 App_A § 3.2.(2) |  |  |  | [ > of 15% ref or 5 PPM ] | 60 App_F § 5.2.3 | [12 empty] | LEVEL 2 = 25 - 75% of max concentration (Test can overlap)
CO | [5 empty] | none | [9 empty] | > of 15% ref or 5 PPM | 60 App_F § 5.2.3 | [12 empty] | LEVEL 3 = 50 - 100% of max concentration (Test can overlap)
HG | [ LE  10 % ] | 75 App_A § 5.1.2.2 |  |  |  | none |  | [ diff  0.8 ug/scm ] |  |  |  | 75 App_A § 5.1.2.2 | [17 empty] | Minimum 15 valid runs may reject 5 but report ALL runs - 20 Total
Of the 15 runs, 20% need to be in the above levels
FLOW to LOAD or Gross Heat Rate | [9 empty] | Leak Check | [5 empty] | FUELFLOW to LOAD or Gross Heat Rate
75 App_B § 2.2.5.(a) |  | each QA operating quarter | [7 empty] | 75 App_B § 2.2.2 |  |  |  | DP flow monitors |  | App_D § 2.1.7 | optional - each fuel flow meter QA op quarter | [7 empty] | Every 3 Years |  |  | P60 Proc 2 |  | Minimum of 12 runs NOT 15
75 App_B § 2.2.5.(a).(4) |  | if 2 RATA load levels are defined as normal - use the higher | [11 empty] | Unit can be off-line |  |  | may be used to extend fuel flow meter cals for up to 20 calendar quarters | [12 empty] | All points can be not > the greatest CEMS value during curve
[14 empty] | 30 days apart | [15 empty] | At least 75% of 12 Points must fall within ±25% of regression line
Parameter | STANDARD | [8 empty] | Parameter |  |  |  | STANDARD |  | Parameter | STANDARD | [7 empty] | EPA provides a spreadsheet on selecting the best fit Correlation equation based on the data recorded. This spreadshet can be found at https://www.epa.gov/sites/production/files/2017-05/ps11qa_05042017.zip
| Avg Load |  |  | steam flow |  |  | FLOW |  | Ef | [7 empty] | Avg LOAD |  | eq STEAM |  |  | Ef
FLOW | Lavg ≥ 60 MW |  |  | 500 klb/hr |  |  | un-biased |  | 15 % | FLOW |  |  |  | Manual inspection |  | FUEL FLOW | Lavg > 50 MW |  | 500 klb/hr |  |  | 10%
| Lavg ≥ 60 MW |  |  | 500 klb/hr |  |  | biased |  | 10 % | [7 empty] | Lavg > 50 MW |  | 500 klb/hr |  |  | 15% |  |  | The 5 types of Correlation Model: | [5 empty] | 1) Linear |  |  | 2) Polynomial
| Lavg < 60 MW |  |  | 500 klb/hr |  |  | un-biased |  | 20 % | [21 empty] | 3) Logarithmic |  |  | 4) Exponential |  | 5) Power
| Lavg < 60 MW |  |  | 500 klb/hr |  |  | biased |  | 15 %
Note on BH11: For PM, data is not flagged invalid back to the previous good cal if failed. App_F Proc 2 § 10.4.1
Note on DP20: 75 App_B § 2.3.1.2.(e)
Note on DP21: 75 App_B § 2.3.1.2.(d)
Note on DP24: 75 App_B § 2.3.1.2.(h)
Note on DP26: 75 App_B § 2.3.1.2.(h)
Note on DP28: 75 App_B § 2.3.1.2.(i)
Note on AH31: Brian Perlov: For span values less than 0.3333 "wc the difference method (i.e. < 0.02 'wc ug/scm) is less restrictive.
Note on DP31: 75 App_B § 2.3.1.2.(e)
Note on DP33: 75 App_B § 2.3.1.2.(f)
Note on AH39: Brian Perlov: For span values less than 20 ug/scm the difference method (i.e. < 1.0 ug/scm) is less
Note on X52: 10% of 8 ug/scm = 0.8 ug/scm For reference values less than 8 ug/scm the difference method (i.e. < 0.8 ug/scm) is less restrictive.
Note on BS72: For reference values less than 33.333 ppm the difference method (i.e. > 5 ppm) is less restrictive.
Note on AB76: 5% of 100 ppm= 5 ppm For reference values less than 100 ppm the difference method (i.e. > 5 ppm) is less restrictive.
Note on AZ76: For reference values less than 33.333 ppm the difference method (i.e. > 5 ppm) is less restrictive.
Note on AB78: 5% of 100 ppm= 5 ppm For reference values less than 100 ppm the difference method (i.e. > 5 ppm) is less restrictive.
Note on AZ78: For reference values less than 33.333 ppm the difference method (i.e. > 5 ppm) is less restrictive.
Note on AB80: 5% of 10 %= 0.5 % For reference values less than 10 % the difference method (i.e. < 0.5%) is less restrictive.
Note on AZ80: For reference values less than 33.333 ppm the difference method (i.e. > 5 ppm) is less restrictive.
Note on AB82: 5% of 10 %= 0.5 % For reference values less than 10 % the difference method (i.e. < 0.5%) is less restrictive.
Note on AZ82: For reference values less than 33.333 ppm the difference method (i.e. > 5 ppm) is less restrictive.
Note on AZ84: For reference values less than 33.333 ppm the difference method (i.e. > 5 ppm) is less restrictive.
Note on B86: Brian Perlov: Part 63, Subpart UUUUU
Note on AB86: 10% of 8 ug/scm = 0.8 ug/scm For reference values less than 8 ug/scm the difference method (i.e. < 0.8 ug/scm) is less restrictive.