## NH3 Slip Calc
Compliance with ammonia slip limit shall be demonstrated by using the following calculation procedure:
As = [A - (B * C / 1,000,000)] * [(1,000,000 / B) * D]
Since most ammonia slip (As) calculations require correction to oxygen, the resultant formula would be applied.
As = [A - (B * C / 1,000,000)] * [(1,000,000 / B) * D] * [(20.9 - CF) / (20.9 - O2)]
Where:
As = Ammonia Slip (ppmv @ 15% O2)
A = Ammonia Injection Rate (lbs/hr) / (17 lbs/lbs-mol)
B = Dry Exhaust Gas Flow Rate (lbs/hr) / (29 lbs/lbs-mol)
C = Change in Measured NOx Concentration (ppmv @ 15% O2) Across Catalyst
D = Correction Factor. The correction factor shall be derived annually during compliance testing by comparing the measured and calculated ammonia slip.
CF = O2 Correction Factor
O2 = Measured Exhaust Stack O2 Concentration
Following is how ESC proposes to handle the calculation in the CEMS Controller.
The following channels shall be set up in the controller. (Also referenced are the variables in the
initial equation):
NH3INJ |  | = Ammonia Injection Rate In lbs/hr
NH3MOLE |  | = A = NH3INJ (lb/hr) / 17 (lbs/lbs-mol)
FLOWSCFH |  | = Dry Exhaust Flow Rate in scfh =
HEATIN (mmbtu/hr) * FUELFACT (dscf/mmbtu) * (20.9 / (20.9 - O2))
Where: HEATIN = ((RDGASFL + RCGASFL) / 100 * GASGCV / 10,000
O2 value needs to be full precision / DO NOT ROUND)
TEGASFL |  | = B = (FLOWSCFH (scfh) * K01 (#/scf)) / 29
Total exhaust gas flow rate converted to lb/hr and then divided by constant 29. The K01 is a constant we have used in the past and was supplied to ESC by another client who was using this same equation for ammonia slip.
K02 |  | = D = Correction factor derived annually duing compliance testing. (This is for correcting flow calculated value)
Customer supplied.
Therefore, the final resulting equation is:
As | = [A - (B * C / 1,000,000)] * [(1,000,000 / B) * D] * [(20.9 - CF) / (20.9 - RO2)]
= {NH3NOLE - [TEGASFL * (NOXSCRIN - NOXPPM) / 1,000,000]} * [(1,000,000 / TEGASFL) * K02] * (20.9 - CF) / (20.9 - RO2)
To get a fair number, you can use the following analog input values:
RNOXSCRIN | = | 50 | RNOXSCRIN = Raw NOx reading at SCR Inlet
RNOXLO | = | 5 | RNOXLO = Raw NOx reading at exhaust stack
RNH3INJ | = | 100 | RNH3INJ = Raw reading of NH3 injection rate
RDGASFL | = | 100000 | RDGASFL = Raw reading of duct burner fuel gas flow
RCGASFL | = | 100000 | RCGASFL = Raw reading of combustion turbine fuel gas flow
RO2 | = | 10 | RO2 = Raw O2 reading (Needs to be full precision / DO NOT ROUND)
FUELFACT | = | 8710 | FUELFACT = Natural Gas F-Factor from 40CFR75, Appendix F
GASGCV | = | 1000 | GASGCV = Gas GCV value from monthly sample analysis
K01 | = |  | Customer derived correction factor (#/scf)
K02 | = | 1
CF | = | 15 | O2 Correction Factor supplied in Air Permit
NH3MOLE | = | 5.8824
FLOWSCFH | = | 3340165.1376
TEGASFL | = | 0
As = | {NH3NOLE - [TEGASFL * (NOXSCRIN - NOXPPM) / 1,000,000]} * [(1,000,000 / TEGASFL) * K02] * (20.9 - CF) / (20.9 - RO2)
As = | #DIV/0! | ppm
NOTE: | - Given
- Calculated