## NH3 TONS
Calculation of NH3 TONS from NH3 PPM for oil an gas fired units
First, Calculate Stack Flow rate from fuel flow rate
GAS | OIL
Qs = stack flow rate on dry basis at standard conditions (SCFH) | Qs = stack flow rate on dry basis at standard conditions (SCFH)
Qf = fuel flow (SCFH) | Qf = fuel flow (lb/hr)
Fgas = F factor for gas = 8710 (SCF/MMBTU) | Foil = F factor for oil = 9190 (SCF/MMBTU)
HHV = high heating value of gas - dry (Btu/SCF) aka GCV | HHV = high heating value of gas - dry (Btu/SCF) aka GCV
O2 = concentration of O2 (%) | O2 = concentration of O2 (%)
Then, Calculate NH3 lb/hr
-OR-
E = Emissions in LB/HR
E = Emissions in LB/HR | MW = molecular weight of NH3 = 17.03 lb/lb-mole
K = conversion constant for NH3 = 4.420e-8 | G = ideal gas c factor = 385.27 SCF/lb-mol at 68 °F & 14.696 psia
C = concentration of NH3 in ppm/hr | C = concentration of NH3 in ppm/hr
Qs = stack flow rate on dry basis at standard conditions (SCFH) | Qs = stack flow rate on dry basis at standard conditions (SCFH)
Then Calculate NH3TONS
NH3TONS = NH3 LB/HR * UNITOPHR#100 / 2000
Single Equation

## Ideal Gas Conversion Factor
Calculation of Ideal Gas Conversion Factor
The ideal gas law is the equation of state of a hypothetical ideal gas.
The state of an amount of gas is determined by its pressure, volume, and temperature.
Where:
p = absolute pressure of gas
V = volume
n = about of substance
R = universal gas constant
T = absolute temperature
For n=1, V=RT/P
At standard conditions P=1 atm, T=273 K (=492oR), with the gas constant R=0.0821 L.atm/(g-mol.K)
| V=(0.0821)(273.1)/(1) = 22.4 L/g-mol |  | V= | 22.4215
This is 22.4 L/g-mol, or 22.4 m3/kg-mol at standard conditions, which converted to british units would be
| (22.4)(454 g/lb)/(28.3 L/ft3) = 359 ft3/lb-mol |  | V= | 359.3498
Using the same law one can find the molar volume at other conditions following:
(PV/T)2=(PV/T)1
Assume pressure equals 1 atm, the volume at other (absolute) temperatures would be:
V2=V1(T2/T1)
60 °F = 520 °R |  | V60= 359(520/492)~ 379 ft3/lb-mol
68 °F = 528 °R |  | V68= 359(528/492)~ 385 ft3/lb-mol | V= | 385.2683
70 °F = 530 °R |  | V70= 359(530/492)~ 387 ft3/lb-mol

## Conversion Constant
Calculation of the Conversion Factor
References:
ASTM 3588
40CFR60, Appendix A, Reference Method 19
Where:
K = conversion constant
MW = molecular weight, lb/lb-mole
| G = ideal gas conversion factor, SCF/lb=mol |  |  | 385.27
@ 68 °F and 14 psia
| Pollutant | Molecular Weight (lb/lb-mole) | Conversion Constant (lb/ppm*scf)
| CO | 28 | 7.2676e-08
| NH3 | 17.03 | 4.4203e-08
| NOX | 46.01 | 1.1942e-07
| SO2 | 64 | 1.6612e-07
| SO3 | 80.06 | 2.078e-07
| THC (propane) | 44 | 1.1421e-07
| VOC (methane) | 16 | 4.1529e-08